Personnel Emergency Alarm

Supplemental Information Sheet

Each room is provided with reset-type alarms and an electrically powered personnel emergency alarm system. The system consists of an actuator within the room and audible and visual alarms affixed to the front exterior of the room. Also provided is an extra set of dry contacts for connection to a remote annunciator panel and/or Building Automation System.

The alarm system actuator is a heavy-duty switch, equipped with a red LED

illuminated plastic push-pull button. The actuator is mounted on the interior

wall of the room adjacent to the doorjamb and 12 inches (305 mm) above the floor

level in a recessed foamed-in-place electrical back box in the wall panel. Mounted directly

above the switch is an engraved plate labeled “EMERGENCY ALARM – PULL TO RESET”.

The audible/visual alarm is a dedicated horn-strobe mounted in a recessed

foamed-in-place electrical back box above the door. The horn-strobe has a blue lens, and a high decibel level (minimum 85 dBA) of sound output. Mounted directly above the device is an engraved plate labeled “PERSONNEL EMERGENCY”.