WAC2 - Water Cooled Condensing Unit

Supplemental Information Sheet

Your chamber is equipped with a water condensing unit located on top of the chamber. The water requirements for the condenser are 120 GPH (454 LPH) with a recommended temperature difference of 20°F (6.7°C) between inlet and outlet.  The ideal inlet temperature is 65°F (18.3°C).

The connections will be made at installation.  If there are issues with the connections, contact your service representative.  If no service representative is available, please contact Percival Scientific for instructions.