Q9 – Phenolic Coated Evaporator Coils

Operator’s Manual

505 Research Drive  Perry, Iowa 50220

Toll-free 800.695.2743  515.465.9363  fax 515.465.9464

www.percival-scientific.com

[This page intentionally left blank]

# Introduction

To help customers create better science, Percival Scientific continuously studies and refines the design of its products in order to provide the best possible solutions and equipment in the industry.  As such, changes in the design and/or operation of equipment may occur without publication.  Please feel free to contact Percival Scientific directly for product updates.

Information contained within this supplemental user manual shall supersede any conflicting information contained within the basic chamber user manual.

Please read this manual carefully before proceeding with operation

# Revision Log

| Version | Date | Description |
| --- | --- | --- |
| Rev A | 7/18/2024 | Initial Release |

Introduction	3

Revision Log	4

Warranty Information	6

Definitions	8

General	8

Location	8

Operation	8

Maintenance	9

Troubleshooting	10

Parts and Service	10

# Warranty Information

Equipment Limited Warranty

Thank you for purchasing equipment from Percival Scientific, Inc.  Our goal is to provide every customer with an exceptional ownership experience.  We are committed to providing products and services of the highest quality, and your satisfaction is our top priority.  In support of this objective, we present the following warranty.

Warranty Terms

Percival Scientific, Inc. (hereinafter referred to as Percival) warrants that equipment manufactured by Percival shall be free from defect in material or workmanship, when installed, operated and maintained in accordance with instructions provided by Percival.

Warranty Coverage

- Coverage period shall be twenty-four (24) months from the date of delivery

- Percival’s obligation under this warranty is limited to the repair or replacement of defect at no charge for parts, shipping and labor

- Percival reserves the right to inspect the equipment after a warranty claim is made in order to determine the proper course of corrective action

Exclusions

- Parts or elements damaged from improper installation, including mechanical, electrical and plumbing services, IT infrastructure, inadequate room ventilation, improper water quality, and ambient conditions that are out of specification

- Parts or elements damaged from improper operation

- Parts or elements damaged from improper maintenance

- Parts or elements considered to be consumable, that outlive their normal expected terms of usefulness, such as: light bulbs, filters, desiccant material and CO2 scrubbing media

- Damage resulting from shipment to or relocation within the customer’s facility after equipment has been signed for and ownership is transferred to the customer

- Modification to equipment by the customer without Percival’s consent may void this warranty

- Repair work undertaken without prior consent of Percival may void this warranty

- Damage caused by accident, fire, Force Majeure or Acts of God

Additional Terms

- This warranty is in lieu of any other warranties, expressed or implied, including merchantability or fitness for a particular purpose

- Warranty terms described herein cannot be changed without the expressed, written consent from Percival

- The owner agrees that Percival’s sole liability with respect to defective parts or materials shall be set forth in this warranty, and any claims for incidental or consequential damages are expressly excluded

- This warranty is non-transferable and applies only to the original purchaser

- Repaired or replaced parts shall be warranted only for the unexpired portion of the original warranty, unless otherwise defined

- Parts replaced under warranty shall become the property of Percival

To Make a Warranty Claim

- Document the issue with detailed notes and photographs along with the equipment’s serial number

- Contact Percival’s customer support team at customerservice@percival-scientific.com, parts@percival-scientific.com or 1-800-695-2743

- Once your claim is received, our customer support team will review it and contact you with further instructions

# Definitions

# General

Some applications (such as drosophila and marine) can create conditions inside environmental chambers that are corrosive to copper over time.

The Q9 (Phenolic Coated Evaporate Coils) option provides improved corrosion resistance for refrigeration components housed inside a Percival environmental chamber. Corrosion resistance is achieved through the application of a special phenolic epoxy coating applied to all susceptible refrigeration components inside the controlled environment

In addition to the coating on the standard evaporator coils, it is also applied to dehumidifying evaporator coils, copper refrigeration lines inside the chamber, and thermal expansion valves.

## Location

Phenolic coated refrigeration components are installed in the same method and location as standard equipment.  Prior to installation, the phenolic coating is applied to susceptible parts.

# Operation

Phenolic coating does not change the refrigeration system’s operation.  Refrigeration system performance is only minimally changed.  Coated evaporator coils are estimated to have approximately 1% less capacity than an uncoated system.

# Maintenance

It is recommended to clean and inspect the evaporator coils at least once every 12 months. In extremely dirty environments, cleaning intervals should be reduced to every 3 months (four (4) times per year).

Refer to the chamber’s operation manual for general guidance on refrigeration system maintenance, and how to access the evaporator coils for service.

Coated coils and copper lines must be cleaned according to the following guidelines:

- Flush the coil with water to rinse loose residue.  Allow the system to soak for 10-20 minutes to help dissolve or loosen any surface residue.

- Use an acceptable cleaner, such as:

  - Liquid soap detergent and warm water

  - Lysol

  - Pine-Sol

  - Pine oil or other terpene-based cleaners

- Flush unit with cleaner thoroughly until all signs of residue are eliminated

- Rinse with clean water

- Allow the unit to dry completely prior to turning on power and putting the unit back into service

Avoid:

- Spraying water or cleaning agents onto any components, other than the desired cleaning area.  Electrical components inside the controlled environment could sustain damage.

- Using water under high pressure

- Abrasive products to scour or remove dirt

- Striking the coil with a tool to dislodge or remove soil or residue

- Corrosive, caustic or alkaline cleaners (with a pH < 5.5 or > 8.5)

Damage from improper cleaning may void the warranty.

# Troubleshooting

Temperature control problems stemming from loss of refrigerant charge can result from problems with the phenolic coating.  If there is suspicion the phenolic coating has been compromised, perform a visual inspection (where possible) of coated components.

Conduct a leak detection test to assess areas of the coated components that cannot be visually inspected.

## Parts and Service

Replacement parts can be ordered from Percival Scientific at:

Ph: 1-800-695-2743

Email: parts@percival-scientific.com

For additional questions regarding this product, please contact Percival’s customer support team at:

Phone: 1-800-695-2743

Email: customerservice@percival-scientific.com

Please have your chamber serial number available for faster and more efficient customer service.